## HOME
SPIRAL ROUND AND FLAT OVAL DUCT CALCULATOR
1.) FIND AN AVAILABLE ROUND OR OVAL SPIRAL SIZE FOR A GIVEN CFM AND FRICTION LOSS
2.) FIND AN AVAILABLE OVAL SPIRAL SIZE FOR A GIVEN ROUND DUCT SIZE
3.) FIND AN AVAILABLE ROUND OR OVAL SPIRAL FOR A GIVEN OVAL DUCT SIZE
4.) FIND AN AVAILABLE ROUND OR OVAL SPIRAL SIZE FOR A GIVEN RECTANGULAR DUCT SIZE
Calculations are based on STP and an absolute roughness factor of .0003 ft.
1 | ROUND AND OVAL SPIRAL DUCT CALCULATOR - INSERT CFM AND FRICTION LOSS IN THE YELLOW BOXES
INSERT CFM |  | 30000 | AVAILABLE SPIRAL FLAT OVAL SIZES
INSERT FRICTION LOSS PER 100' OF DUCT |  | 0.1
CALCULATED HYDRAULIC DIAMETER (IN) |  | 50.3605 | Major Axis |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5488 | 77.124 | 72.8408 | 68.5576 | 64.2744
AVAILABLE SPIRAL DIAMETER (IN) |  | 50 | Minor Axis |  | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 36
VELOCITY (AVAILABLE DIAMETER) FPM |  | 2200.1528 | Velocity (FPM) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1964.4221 | 2037.1785 | 2046.2731 | 2074.0505 | 2122.0609
2 | USER DEFINED ROUND DIAMETER TO AVAILABLE OVAL SPIRAL SIZES - INPUT DIAMETER IN THE YELLOW BOX
INSERT ROUND DIAMETER |  | 34 | AVAILABLE SPIRAL FLAT OVAL SIZES
|  |  | Major Axis |  | 0 | 0 | 0 | 0 | 0 | 0 | 69.4072 | 58.8408 | 54.5576 | 47.1328 | #N/A | 41.708 | 37.4248 | 36.2832 | 0 | 0 | 0
|  |  | Minor Axis |  | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 36
VELOCITY FPM |  | 3172.0773 | Velocity (FPM) |  | 0 | 0 | 0 | 0 | 0 | 0 | 2728.3641 | 2910.255 | 2864.7823 | 3086.6341 | #N/A | 3065.9877 | 3274.0369 | 3216.5976 | 0 | 0 | 0
INSERT CFM IF KNOWN (NOT REQ'D) |  | 20000 | Friction Loss |  | 4: 0.33258; 8: Insert CFM in the blue box if a friction loss calculation is desired
3 | USER DEFINED OVAL SIZE TO AVAILABLE SPIRAL ROUND AND AVAILABLE OVAL SPIRAL SIZES - INPUT MAJOR AND MINOR AXIS IN THE YELLOW BOXES
INSERT MAJOR AXIS |  | 54 | AVAILABLE SPIRAL FLAT OVAL SIZES
INSERT MINOR AXIS |  | 18
CALCULATED HYDRAULIC DIAMETER (IN) |  | 32.375 | Major Axis |  | 0 | 0 | 0 | 0 | 0 | 73.6904 | 63.124 | 52.5576 | 48.2744 | 43.9912 | #N/A | 38.5664 | 34.2832 | 0 | 0 | 0 | 0
AVAILABLE SPIRAL DIAMETER (IN) |  | 32 | Minor Axis |  | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 36
VELOCITY (AVAILABLE DIAMETER) FPM |  | 1749.2472 | Velocity (FPM) |  | 0 | 0 | 0 | 0 | 0 | 1455.1275 | 1507.7801 | 1642.8859 | 1637.0184 | 1666.7824 | #N/A | 1678.9933 | 1818.9094 | 0 | 0 | 0 | 0
INSERT CFM IF KNOWN (NOT REQ'D) |  | 10000 | Friction Loss |  | 4: 0.11395; 8: Insert CFM in the blue box if a friction loss calculation is desired
4 | USER DEFINED RECTANGLE SIZE TOAVAILABLE ROUND SPIRAL AND AVAILABLE OVAL SPIRAL SIZES - INPUT RECTANGLE WIDTH AND DEPTH IN THE YELLOW BOXES
INSERT RECTANGULAR WIDTH |  | 36 | AVAILABLE SPIRAL FLAT OVAL SIZES
INSERT RECTANGULAR DEPTH |  | 18
CALCULATED HYDRAULIC DIAMETER (IN) |  | 27.4207 | Major Axis |  | 0 | 0 | 0 | 0 | 62.2656 | 51.6992 | 44.2744 | 36.8496 | 34.1372 | 31.4248 | #N/A | 0 | 0 | 0 | 0 | 0 | 0
AVAILABLE SPIRAL DIAMETER (IN) |  | 27 | Minor Axis |  | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 36
VELOCITY (AVAILABLE DIAMETER) FPM |  | 2438.4453 | Velocity (FPM) |  | 0 | 0 | 0 | 0 | 2010.3735 | 2112.2819 | 2203.6787 | 2425.2125 | 2412.4482 | 2451.1506 | #N/A | 0 | 0 | 0 | 0 | 0 | 0
INSERT CFM IF KNOWN (NOT REQ'D) |  | 10000 | Friction Loss |  | 4: 0.26231; 8: Insert CFM in the blue box if a friction loss calculation is desired
Eastern Sheet Metal (ESM), does not warrant the information in the Spiral Round and Flat Oval Duct Calculator (Calculator) to be free of errors. The Calculator is provided “as is” without warranty of any kind, either expressed or implied. The entire risk as to the quality and performance of the Calculator and data is with you. In no event will ESM or the developer of the Calculator be liable to you for any damages, including without limitation any lost profits, lost savings or other incidental or consequential damages arising out of the use or inability to use the Calculaor and the data provided.

## CALC
OVAL TABLE | [6 empty] | FORMULA 2 | [5 empty] | FORMULA 1 |  |  |  | SPIRAL ROUNDING |  |  | FORMULA 2
SPIR | MINOR | RANGE | HYD | MAJOR | AREA | PERIMETER | MINOR | [5 empty] | P | CFM |  |  | RANGE | AVAIL |  | MINOR
0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | #REF! | #REF! | #REF! | #REF! |  | 0.1 | 30000 |  |  | 2.5 | 3 |  | 4 | 54 | 0 | #REF! | #REF!
8 | 4 | 6.5 | 6.6908 | 10.2832 | 37.6992 | 25.1328 | 6 | #REF! | #REF! |  |  |  |  | 321018738.6426 |  |  | 3.5 | 4 |  | 6 | 54 | 0
9 | 4 | 6.9223 | 7.1537 | 11.854 | 43.9824 | 28.2744 | 8 | #REF! | #REF! |  |  |  |  | 35034701.0605 | 350347010.605 |  | 4.5 | 5 |  | 8 | 54 | 0
10 | 4 | 7.364 | 7.5742 | 13.4248 | 50.2656 | 31.416 | 10 | #REF! | #REF! |  |  |  |  | HD | 50.3605 |  | 5.5 | 6 |  | 10 | 54 | 0
11 | 4 | 7.7675 | 7.9609 | 14.9956 | 56.5488 | 34.5576 | 12 | #REF! | #REF! |  |  |  |  | AVAILABLE | 50 |  | 6.5 | 7 |  | 12 | 54 | 0
12 | 4 | 8.1403 | 8.3198 | 16.5664 | 62.832 | 37.6992 | 14 | #REF! | #REF! |  |  |  |  | AREA | 13.6354 |  | 7.5 | 8 |  | 14 | 54 | 0
13 | 4 | 8.4876 | 8.6555 | 18.1372 | 69.1152 | 40.8408 | 16 | #REF! | #REF! |  |  |  |  | VELOCITY | 2200.1528 |  | 8.5 | 9 |  | 16 | 54 | 0
14 | 4 | 8.8135 | 8.9715 | 19.708 | 75.3984 | 43.9824 | 18 | #REF! | #REF! | [7 empty] | 9.5 | 10 |  | 18 | 54 | 0
15 | 4 | 9.1209 | 9.2704 | 21.2788 | 81.6816 | 47.124 | 20 | #REF! | #REF! | [7 empty] | 10.5 | 11 |  | 20 | 54 | 0
16 | 4 | 9.4124 | 9.5545 | 22.8496 | 87.9648 | 50.2656 | 22 | #REF! | #REF! | [7 empty] | 11.5 | 12 |  | 22 | 54 | 0
17 | 4 | 9.69 | 9.8254 | 24.4204 | 94.248 | 53.4072 | 24 | #REF! | #REF! | [7 empty] | 12.5 | 13 |  | 24 | 54 | 0
18 | 4 | 9.9551 | 10.0847 | 25.9912 | 100.5312 | 56.5488 | 26 | #REF! | #REF! | [7 empty] | 13.5 | 14 |  | 26 | 54 | 0
19 | 4 | 10.2091 | 10.3335 | 27.562 | 106.8144 | 59.6904 | 28 | #REF! | #REF! | [7 empty] | 14.5 | 15 |  | 28 | 54 | 0
20 | 4 | 10.4532 | 10.5729 | 29.1328 | 113.0976 | 62.832 | 30 | #REF! | #REF! | [7 empty] | 15.5 | 16 |  | 30 | 54 | 0
21 | 4 | 10.6883 | 10.8037 | 30.7036 | 119.3808 | 65.9736 | 32 | #REF! | #REF! | [7 empty] | 16.5 | 17 |  | 32 | 54 | 82.2656
22 | 4 | 10.9152 | 11.0267 | 32.2744 | 125.664 | 69.1152 | 34 | #REF! | #REF! | [7 empty] | 17.5 | 18 |  | 34 | 54 | 77.9824
0 | 4 | 11.2633 | 11.5 | 0 | 0 | 0 | 36 | #REF! | #REF! | [7 empty] | 18.5 | 19 |  | 36 | 54 | 73.6992
0 | 6 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 19.5 | 20
9 | 6 | 8.2 | 8.3704 | 10.7124 | 56.5488 | 28.2744 | [10 empty] | 20.5 | 21
10 | 6 | 8.6739 | 8.9774 | 12.2832 | 65.9736 | 31.416 | [10 empty] | 21.5 | 22
11 | 6 | 9.2532 | 9.529 | 13.854 | 75.3984 | 34.5576 | FORMULA 3 |  |  |  |  | FORMULA 6 |  |  |  |  | 22.5 | 23
12 | 6 | 9.7826 | 10.0362 | 15.4248 | 84.8232 | 37.6992 | MINOR |  |  |  |  | MINOR |  |  |  |  | 23.5 | 24
13 | 6 | 10.2716 | 10.507 | 16.9956 | 94.248 | 40.8408 | 4 | #REF! | #REF! | #REF! | #REF! | 4 | #REF! | #REF! | #REF! | #REF! | 24.5 | 25
14 | 6 | 10.7271 | 10.9472 | 18.5664 | 103.6728 | 43.9824 | 6 | #REF! | #REF! |  |  | 6 | #REF! | #REF! |  |  | 25.5 | 26
15 | 6 | 11.1543 | 11.3613 | 20.1372 | 113.0976 | 47.124 | 8 | #REF! | #REF! |  |  | 8 | #REF! | #REF! |  |  | 26.5 | 27
16 | 6 | 11.5572 | 11.753 | 21.708 | 122.5224 | 50.2656 | 10 | #REF! | #REF! |  |  | 10 | #REF! | #REF! |  |  | 27.5 | 28
17 | 6 | 11.939 | 12.125 | 23.2788 | 131.9472 | 53.4072 | 12 | #REF! | #REF! |  |  | 12 | #REF! | #REF! |  |  | 28.5 | 29
18 | 6 | 12.3023 | 12.4797 | 24.8496 | 141.372 | 56.5488 | 14 | #REF! | #REF! |  |  | 14 | #REF! | #REF! |  |  | 29.5 | 30
19 | 6 | 12.6493 | 12.8189 | 26.4204 | 150.7968 | 59.6904 | 16 | #REF! | #REF! |  |  | 16 | #REF! | #REF! |  |  | 31 | 32
20 | 6 | 12.9816 | 13.1443 | 27.9912 | 160.2216 | 62.832 | 18 | #REF! | #REF! |  |  | 18 | #REF! | #REF! |  |  | 33 | 34
21 | 6 | 13.3007 | 13.4572 | 29.562 | 169.6464 | 65.9736 | 20 | #REF! | #REF! |  |  | 20 | #REF! | #REF! |  |  | 35 | 36
22 | 6 | 13.608 | 13.7588 | 31.1328 | 179.0712 | 69.1152 | 22 | #REF! | #REF! |  |  | 22 | #REF! | #REF! |  |  | 37 | 38
23 | 6 | 13.9044 | 14.05 | 32.7036 | 188.496 | 72.2568 | 24 | #REF! | #REF! |  |  | 24 | #REF! | #REF! |  |  | 39 | 40
24 | 6 | 14.1909 | 14.3317 | 34.2744 | 197.9208 | 75.3984 | 26 | #REF! | #REF! |  |  | 26 | #REF! | #REF! |  |  | 41 | 42
25 | 6 | 14.4682 | 14.6047 | 35.8452 | 207.3456 | 78.54 | 28 | #REF! | #REF! |  |  | 28 | #REF! | #REF! |  |  | 43 | 44
26 | 6 | 14.7372 | 14.8696 | 37.416 | 216.7704 | 81.6816 | 30 | #REF! | #REF! |  |  | 30 | #REF! | #REF! |  |  | 45 | 46
27 | 6 | 14.9984 | 15.1271 | 38.9868 | 226.1952 | 84.8232 | 32 | #REF! | #REF! |  |  | 32 | #REF! | #REF! |  |  | 47 | 48
28 | 6 | 15.2523 | 15.3775 | 40.5576 | 235.62 | 87.9648 | 34 | #REF! | #REF! |  |  | 34 | #REF! | #REF! |  |  | 49 | 50
29 | 6 | 15.4995 | 15.6215 | 42.1284 | 245.0448 | 91.1064 | 36 | #REF! | #REF! |  |  | 36 | #REF! | #REF! |  |  | 51 | 52
30 | 6 | 15.7404 | 15.8594 | 43.6992 | 254.4696 | 94.248 | [10 empty] | 53 | 54
32 | 6 | 16.0888 | 16.3183 | 46.8408 | 273.3192 | 100.5312 | FORMULA 4 | [9 empty] | 55 | 56
34 | 6 | 16.5376 | 16.757 | 49.9824 | 292.1688 | 106.8144 | 18 | 32 | 32.375 | 54 | 902.4696 | 128.5486 |  |  |  |  | 57 | 58
36 | 6 | 16.9672 | 17.1775 | 53.124 | 311.0184 | 113.0976 | MINOR | ACTUAL | CALC | MAJOR | [6 empty] | 59 | 60
38 | 6 | 17.3796 | 17.5817 | 56.2656 | 329.868 | 119.3808 | [10 empty] | 61 | 62
40 | 6 | 17.7764 | 17.9711 | 59.4072 | 348.7176 | 125.664 | [10 empty] | 63 | 64
42 | 6 | 18.1591 | 18.3471 | 62.5488 | 367.5672 | 131.9472 | [10 empty] | 65 | 66
44 | 6 | 18.5289 | 18.7107 | 65.6904 | 386.4168 | 138.2304 | FORMULA 5 | [9 empty] | 67 | 68
46 | 6 | 18.8869 | 19.0631 | 68.832 | 405.2664 | 144.5136 | W | D | HYD D | LOOKUP | [6 empty] | 69 | 70
48 | 6 | 19.234 | 19.4049 | 71.9736 | 424.116 | 150.7968 | 36 | 18 | 27.4207 | 27 | [6 empty] | 71 | 72 | http://www.engineeringtoolbox.com/duct-friction-pressure-loss-d_444.html
0 | 6 | 19.7025 | 20 | 0 | 0 | 0 | [10 empty] | 73 | 74
0 | 8 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 75 | 76
10 | 8 | 9.5 | 9.7588 | 11.1416 | 75.3984 | 31.416 | [10 empty] | 77 | 78
11 | 8 | 10.1258 | 10.4927 | 12.7124 | 87.9648 | 34.5576 | [10 empty] | 79 | 80
12 | 8 | 10.8267 | 11.1606 | 14.2832 | 100.5312 | 37.6992 | [10 empty] | 81 | 82
13 | 8 | 11.4679 | 11.7752 | 15.854 | 113.0976 | 40.8408 | [10 empty] | 83 | 84
14 | 8 | 12.0605 | 12.3458 | 17.4248 | 125.664 | 43.9824 | [10 empty] | 84.001 | NA
15 | 8 | 12.6126 | 12.8795 | 18.9956 | 138.2304 | 47.124
16 | 8 | 13.1306 | 13.3816 | 20.5664 | 150.7968 | 50.2656
17 | 8 | 13.6191 | 13.8565 | 22.1372 | 163.3632 | 53.4072
18 | 8 | 14.082 | 14.3075 | 23.708 | 175.9296 | 56.5488
19 | 8 | 14.5224 | 14.7374 | 25.2788 | 188.496 | 59.6904
20 | 8 | 14.9429 | 15.1485 | 26.8496 | 201.0624 | 62.832
21 | 8 | 15.3456 | 15.5427 | 28.4204 | 213.6288 | 65.9736
22 | 8 | 15.7322 | 15.9217 | 29.9912 | 226.1952 | 69.1152
23 | 8 | 16.1043 | 16.287 | 31.562 | 238.7616 | 72.2568
24 | 8 | 16.4633 | 16.6396 | 33.1328 | 251.328 | 75.3984
25 | 8 | 16.8101 | 16.9806 | 34.7036 | 263.8944 | 78.54
26 | 8 | 17.1458 | 17.311 | 36.2744 | 276.4608 | 81.6816
27 | 8 | 17.4712 | 17.6315 | 37.8452 | 289.0272 | 84.8232
28 | 8 | 17.7872 | 17.9429 | 39.416 | 301.5936 | 87.9648
29 | 8 | 18.0944 | 18.2458 | 40.9868 | 314.16 | 91.1064
30 | 8 | 18.3933 | 18.5408 | 42.5576 | 326.7264 | 94.248
32 | 8 | 18.8249 | 19.109 | 45.6992 | 351.8592 | 100.5312
34 | 8 | 19.3799 | 19.6509 | 48.8408 | 376.992 | 106.8144
36 | 8 | 19.9102 | 20.1694 | 51.9824 | 402.1248 | 113.0976
38 | 8 | 20.4183 | 20.6671 | 55.124 | 427.2576 | 119.3808
40 | 8 | 20.9065 | 21.1458 | 58.2656 | 452.3904 | 125.664
42 | 8 | 21.3766 | 21.6074 | 61.4072 | 477.5232 | 131.9472
44 | 8 | 21.8304 | 22.0534 | 64.5488 | 502.656 | 138.2304
46 | 8 | 22.2692 | 22.485 | 67.6904 | 527.7888 | 144.5136
48 | 8 | 22.6941 | 22.9033 | 70.832 | 552.9216 | 150.7968
50 | 8 | 23.1064 | 23.3094 | 73.9736 | 578.0544 | 157.08
0 | 8 | 23.6547 | 24 | 0 | 0 | 0
0 | 10 | 0 | 0 | 0 | 0 | 0
12 | 10 | 17.9017 | 11.8035 | 13.1416 | 109.956 | 37.6992
13 | 10 | 12.1901 | 12.5766 | 14.7124 | 125.664 | 40.8408
14 | 10 | 12.9328 | 13.2889 | 16.2832 | 141.372 | 43.9824
15 | 10 | 13.6198 | 13.9507 | 17.854 | 157.08 | 47.124
16 | 10 | 14.2604 | 14.57 | 19.4248 | 172.788 | 50.2656
17 | 10 | 14.8615 | 15.1529 | 20.9956 | 188.496 | 53.4072
18 | 10 | 15.4286 | 15.7042 | 22.5664 | 204.204 | 56.5488
19 | 10 | 15.966 | 16.2279 | 24.1372 | 219.912 | 59.6904
20 | 10 | 16.4774 | 16.727 | 25.708 | 235.62 | 62.832
21 | 10 | 16.9657 | 17.2044 | 27.2788 | 251.328 | 65.9736
22 | 10 | 17.4333 | 17.6622 | 28.8496 | 267.036 | 69.1152
23 | 10 | 17.8822 | 18.1023 | 30.4204 | 282.744 | 72.2568
24 | 10 | 18.3143 | 18.5263 | 31.9912 | 298.452 | 75.3984
25 | 10 | 18.7309 | 18.9356 | 33.562 | 314.16 | 78.54
26 | 10 | 19.1335 | 19.3314 | 35.1328 | 329.868 | 81.6816
27 | 10 | 19.5231 | 19.7148 | 36.7036 | 345.576 | 84.8232
28 | 10 | 19.9008 | 20.0868 | 38.2744 | 361.284 | 87.9648
29 | 10 | 20.2674 | 20.4481 | 39.8452 | 376.992 | 91.1064
30 | 10 | 20.6238 | 20.7994 | 41.416 | 392.7 | 94.248
32 | 10 | 21.1373 | 21.4751 | 44.5576 | 424.116 | 100.5312
34 | 10 | 21.7966 | 22.1181 | 47.6992 | 455.532 | 106.8144
36 | 10 | 22.4253 | 22.7324 | 50.8408 | 486.948 | 113.0976
38 | 10 | 23.0266 | 23.3209 | 53.9824 | 518.364 | 119.3808
40 | 10 | 23.6035 | 23.8862 | 57.124 | 549.78 | 125.664
42 | 10 | 24.1584 | 24.4306 | 60.2656 | 581.196 | 131.9472
44 | 10 | 24.6932 | 24.9558 | 63.4072 | 612.612 | 138.2304
46 | 10 | 25.2097 | 25.4636 | 66.5488 | 644.028 | 144.5136
48 | 10 | 25.7095 | 25.9554 | 69.6904 | 675.444 | 150.7968
50 | 10 | 26.1938 | 26.4323 | 72.832 | 706.86 | 157.08
0 | 10 | 26.7161 | 27 | 0 | 0 | 0
0 | 12 | 0 | 0 | 0 | 0 | 0
13 | 12 | 12.5 | 12.9661 | 13.5708 | 131.9472 | 40.8408
14 | 12 | 13.401 | 13.8359 | 15.1416 | 150.7968 | 43.9824
15 | 12 | 14.237 | 14.6382 | 16.7124 | 169.6464 | 47.124
16 | 12 | 15.0112 | 15.3843 | 18.2832 | 188.496 | 50.2656
17 | 12 | 15.7336 | 16.083 | 19.854 | 207.3456 | 53.4072
18 | 12 | 16.4119 | 16.7409 | 21.4248 | 226.1952 | 56.5488
19 | 12 | 17.0521 | 17.3634 | 22.9956 | 245.0448 | 59.6904
20 | 12 | 17.6591 | 17.9548 | 24.5664 | 263.8944 | 62.832
21 | 12 | 18.2367 | 18.5187 | 26.1372 | 282.744 | 65.9736
22 | 12 | 18.7883 | 19.058 | 27.708 | 301.5936 | 69.1152
23 | 12 | 19.3166 | 19.5752 | 29.2788 | 320.4432 | 72.2568
24 | 12 | 19.8238 | 20.0724 | 30.8496 | 339.2928 | 75.3984
25 | 12 | 20.312 | 20.5515 | 32.4204 | 358.1424 | 78.54
26 | 12 | 20.7827 | 21.014 | 33.9912 | 376.992 | 81.6816
27 | 12 | 21.2376 | 21.4612 | 35.562 | 395.8416 | 84.8232
28 | 12 | 21.6778 | 21.8944 | 37.1328 | 414.6912 | 87.9648
29 | 12 | 22.1045 | 22.3146 | 38.7036 | 433.5408 | 91.1064
30 | 12 | 22.5186 | 22.7227 | 40.2744 | 452.3904 | 94.248
32 | 12 | 23.1143 | 23.506 | 43.416 | 490.0896 | 100.5312
34 | 12 | 23.878 | 24.25 | 46.5576 | 527.7888 | 106.8144
36 | 12 | 24.6047 | 24.9593 | 49.6992 | 565.488 | 113.0976
38 | 12 | 25.2986 | 25.6378 | 52.8408 | 603.1872 | 119.3808
40 | 12 | 25.9632 | 26.2886 | 55.9824 | 640.8864 | 125.664
42 | 12 | 26.6015 | 26.9144 | 59.124 | 678.5856 | 131.9472
44 | 12 | 27.216 | 27.5175 | 62.2656 | 716.2848 | 138.2304
46 | 12 | 27.8087 | 28.1 | 65.4072 | 753.984 | 144.5136
48 | 12 | 28.3817 | 28.6634 | 68.5488 | 791.6832 | 150.7968
50 | 12 | 28.9364 | 29.2094 | 71.6904 | 829.3824 | 157.08
52 | 12 | 29.4744 | 29.7393 | 74.832 | 867.0816 | 163.3632
0 | 12 | 30.0196 | 30.3 | 0 | 0 | 0
0 | 14 | 0 | 0 | 0 | 0 | 0
15 | 14 | 14.5 | 14.9747 | 15.5708 | 175.9296 | 47.124
16 | 14 | 15.4177 | 15.8607 | 17.1416 | 197.9208 | 50.2656
17 | 14 | 16.273 | 16.6854 | 18.7124 | 219.912 | 53.4072
18 | 14 | 17.0719 | 17.4583 | 20.2832 | 241.9032 | 56.5488
19 | 14 | 17.8224 | 18.1865 | 21.854 | 263.8944 | 59.6904
20 | 14 | 18.5312 | 18.8759 | 23.4248 | 285.8856 | 62.832
21 | 14 | 19.2034 | 19.531 | 24.9956 | 307.8768 | 65.9736
22 | 14 | 19.8434 | 20.1558 | 26.5664 | 329.868 | 69.1152
23 | 14 | 20.4547 | 20.7536 | 28.1372 | 351.8592 | 72.2568
24 | 14 | 21.0402 | 21.3269 | 29.708 | 373.8504 | 75.3984
25 | 14 | 21.6025 | 21.8781 | 31.2788 | 395.8416 | 78.54
26 | 14 | 22.1437 | 22.4092 | 32.8496 | 417.8328 | 81.6816
27 | 14 | 22.6656 | 22.922 | 34.4204 | 439.824 | 84.8232
28 | 14 | 23.1699 | 23.4179 | 35.9912 | 461.8152 | 87.9648
29 | 14 | 23.658 | 23.8981 | 37.562 | 483.8064 | 91.1064
30 | 14 | 24.1311 | 24.364 | 39.1328 | 505.7976 | 94.248
32 | 14 | 24.8103 | 25.2566 | 42.2744 | 549.78 | 100.5312
34 | 14 | 25.6795 | 26.1025 | 45.416 | 593.7624 | 106.8144
36 | 14 | 26.505 | 26.9075 | 48.5576 | 637.7448 | 113.0976
38 | 14 | 27.2918 | 27.6761 | 51.6992 | 681.7272 | 119.3808
40 | 14 | 28.0442 | 28.4123 | 54.8408 | 725.7096 | 125.664
42 | 14 | 28.7657 | 29.1192 | 57.9824 | 769.692 | 131.9472
44 | 14 | 29.4595 | 29.7997 | 61.124 | 813.6744 | 138.2304
46 | 14 | 30.128 | 30.4562 | 64.2656 | 857.6568 | 144.5136
48 | 14 | 30.7734 | 31.0906 | 67.4072 | 901.6392 | 150.7968
50 | 14 | 31.3977 | 31.7048 | 70.5488 | 945.6216 | 157.08
52 | 14 | 32.0025 | 32.3003 | 73.6904 | 989.604 | 163.3632
0 | 14 | 32.6001 | 32.9 | 0 | 0 | 0
0 | 16 | 0 | 0 | 0 | 0 | 0
17 | 16 | 16.5 | 16.9818 | 17.5708 | 226.1952 | 53.4072
18 | 16 | 17.4311 | 17.8804 | 19.1416 | 251.328 | 56.5488
19 | 16 | 18.3017 | 18.723 | 20.7124 | 276.4608 | 59.6904
20 | 16 | 19.1203 | 19.5176 | 22.2832 | 301.5936 | 62.832
21 | 16 | 19.8938 | 20.27 | 23.854 | 326.7264 | 65.9736
22 | 16 | 20.6278 | 20.9855 | 25.4248 | 351.8592 | 69.1152
23 | 16 | 21.3268 | 21.668 | 26.9956 | 376.992 | 72.2568
24 | 16 | 21.9946 | 22.3212 | 28.5664 | 402.1248 | 75.3984
25 | 16 | 22.6345 | 22.9477 | 30.1372 | 427.2576 | 78.54
26 | 16 | 23.249 | 23.5503 | 31.708 | 452.3904 | 81.6816
27 | 16 | 23.8406 | 24.131 | 33.2788 | 477.5232 | 84.8232
28 | 16 | 24.4113 | 24.6916 | 34.8496 | 502.656 | 87.9648
29 | 16 | 24.9627 | 25.2338 | 36.4204 | 527.7888 | 91.1064
30 | 16 | 25.4964 | 25.759 | 37.9912 | 552.9216 | 94.248
32 | 16 | 26.2611 | 26.7633 | 41.1328 | 603.1872 | 100.5312
34 | 16 | 27.2381 | 27.713 | 44.2744 | 653.4528 | 106.8144
36 | 16 | 28.164 | 28.6149 | 47.416 | 703.7184 | 113.0976
38 | 16 | 29.0448 | 29.4747 | 50.5576 | 753.984 | 119.3808
40 | 16 | 29.8858 | 30.2969 | 53.6992 | 804.2496 | 125.664
42 | 16 | 30.6912 | 31.0854 | 56.8408 | 854.5152 | 131.9472
44 | 16 | 31.4644 | 31.8435 | 59.9824 | 904.7808 | 138.2304
46 | 16 | 32.2087 | 32.5739 | 63.124 | 955.0464 | 144.5136
48 | 16 | 32.9265 | 33.2791 | 66.2656 | 1005.312 | 150.7968
50 | 16 | 33.6201 | 33.9612 | 69.4072 | 1055.5776 | 157.08
52 | 16 | 34.2916 | 34.622 | 72.5488 | 1105.8432 | 163.3632
54 | 16 | 34.9425 | 35.263 | 75.6904 | 1156.1088 | 169.6464
56 | 16 | 35.5744 | 35.8859 | 78.832 | 1206.3744 | 175.9296
0 | 16 | 36.3 | 36.5 | 0 | 0 | 0
0 | 18 | 0 | 0 | 0 | 0 | 0
20 | 18 | 19 | 19.8966 | 21.1416 | 311.0184 | 62.832
21 | 18 | 20.3252 | 20.7538 | 22.7124 | 339.2928 | 65.9736
22 | 18 | 21.16 | 21.5662 | 24.2832 | 367.5672 | 69.1152
23 | 18 | 21.9526 | 22.339 | 25.854 | 395.8416 | 72.2568
24 | 18 | 22.7077 | 23.0765 | 27.4248 | 424.116 | 75.3984
25 | 18 | 23.4294 | 23.7824 | 28.9956 | 452.3904 | 78.54
26 | 18 | 24.1211 | 24.4598 | 30.5664 | 480.6648 | 81.6816
27 | 18 | 24.7855 | 25.1113 | 32.1372 | 508.9392 | 84.8232
28 | 18 | 25.4253 | 25.7393 | 33.708 | 537.2136 | 87.9648
29 | 18 | 26.0425 | 26.3457 | 35.2788 | 565.488 | 91.1064
30 | 18 | 26.6389 | 26.9322 | 36.8496 | 593.7624 | 94.248
32 | 18 | 27.4919 | 28.0516 | 39.9912 | 650.3112 | 100.5312
34 | 18 | 28.5796 | 29.1077 | 43.1328 | 706.86 | 106.8144
36 | 18 | 29.6082 | 30.1087 | 46.2744 | 763.4088 | 113.0976
38 | 18 | 30.5849 | 31.0612 | 49.416 | 819.9576 | 119.3808
40 | 18 | 31.5159 | 31.9706 | 52.5576 | 876.5064 | 125.664
42 | 18 | 32.4061 | 32.8416 | 55.6992 | 933.0552 | 131.9472
44 | 18 | 33.2597 | 33.6778 | 58.8408 | 989.604 | 138.2304
46 | 18 | 34.0803 | 34.4827 | 61.9824 | 1046.1528 | 144.5136
48 | 18 | 34.8709 | 35.259 | 65.124 | 1102.7016 | 150.7968
50 | 18 | 35.634 | 36.0091 | 68.2656 | 1159.2504 | 157.08
52 | 18 | 36.3721 | 36.7351 | 71.4072 | 1215.7992 | 163.3632
54 | 18 | 37.0871 | 37.439 | 74.5488 | 1272.348 | 169.6464
56 | 18 | 37.7806 | 38.1223 | 77.6904 | 1328.8968 | 175.9296
58 | 18 | 38.4544 | 38.7865 | 80.832 | 1385.4456 | 182.2128
0 | 18 | 39.1932 | 39.6 | 0 | 0 | 0
0 | 20 | 0 | 0 | 0 | 0 | 0
23 | 20 | 22.4 | 22.7796 | 24.7124 | 408.408 | 72.2568
24 | 20 | 23.1933 | 23.607 | 26.2832 | 439.824 | 75.3984
25 | 20 | 24.002 | 24.3969 | 27.854 | 471.24 | 78.54
26 | 20 | 24.7751 | 25.1533 | 29.4248 | 502.656 | 81.6816
27 | 20 | 25.5163 | 25.8793 | 30.9956 | 534.072 | 84.8232
28 | 20 | 26.2286 | 26.5778 | 32.5664 | 565.488 | 87.9648
29 | 20 | 26.9145 | 27.2511 | 34.1372 | 596.904 | 91.1064
30 | 20 | 27.5763 | 27.9014 | 35.708 | 628.32 | 94.248
32 | 20 | 28.5207 | 29.14 | 38.8496 | 691.152 | 100.5312
34 | 20 | 29.7229 | 30.3058 | 41.9912 | 753.984 | 106.8144
36 | 20 | 30.8571 | 31.4084 | 45.1328 | 816.816 | 113.0976
38 | 20 | 31.9321 | 32.4557 | 48.2744 | 879.648 | 119.3808
40 | 20 | 32.9549 | 33.4541 | 51.416 | 942.48 | 125.664
42 | 20 | 33.9314 | 34.4088 | 54.5576 | 1005.312 | 131.9472
44 | 20 | 34.8666 | 35.3244 | 57.6992 | 1068.144 | 138.2304
46 | 20 | 35.7644 | 36.2045 | 60.8408 | 1130.976 | 144.5136
48 | 20 | 36.6285 | 37.0525 | 63.9824 | 1193.808 | 150.7968
50 | 20 | 37.4618 | 37.8711 | 67.124 | 1256.64 | 157.08
52 | 20 | 38.267 | 38.6628 | 70.2656 | 1319.472 | 163.3632
54 | 20 | 39.0462 | 39.4296 | 73.4072 | 1382.304 | 169.6464
56 | 20 | 39.8016 | 40.1735 | 76.5488 | 1445.136 | 175.9296
58 | 20 | 40.5348 | 40.8961 | 79.6904 | 1507.968 | 182.2128
0 | 20 | 41.2481 | 41.6 | 0 | 0 | 0
0 | 22 | 0 | 0 | 0 | 0 | 0
24 | 22 | 23.6 | 23.9219 | 25.1416 | 449.2488 | 75.3984
25 | 22 | 24.3617 | 24.8015 | 26.7124 | 483.8064 | 78.54
26 | 22 | 25.2216 | 25.6417 | 28.2832 | 518.364 | 81.6816
27 | 22 | 26.0441 | 26.4465 | 29.854 | 552.9216 | 84.8232
28 | 22 | 26.8328 | 27.2192 | 31.4248 | 587.4792 | 87.9648
29 | 22 | 27.5909 | 27.9627 | 32.9956 | 622.0368 | 91.1064
30 | 22 | 28.3212 | 28.6797 | 34.5664 | 656.5944 | 94.248
32 | 22 | 29.361 | 30.0423 | 37.708 | 725.7096 | 100.5312
34 | 22 | 30.682 | 31.3216 | 40.8496 | 794.8248 | 106.8144
36 | 22 | 31.9253 | 32.529 | 43.9912 | 863.94 | 113.0976
38 | 22 | 33.1013 | 33.6736 | 47.1328 | 933.0552 | 119.3808
40 | 22 | 34.2183 | 34.763 | 50.2744 | 1002.1704 | 125.664
42 | 22 | 35.2831 | 35.8032 | 53.416 | 1071.2856 | 131.9472
44 | 22 | 36.3014 | 36.7995 | 56.5576 | 1140.4008 | 138.2304
46 | 22 | 37.2778 | 37.7561 | 59.6992 | 1209.516 | 144.5136
48 | 22 | 38.2164 | 38.6767 | 62.8408 | 1278.6312 | 150.7968
50 | 22 | 39.1206 | 39.5646 | 65.9824 | 1347.7464 | 157.08
52 | 22 | 39.9935 | 40.4225 | 69.124 | 1416.8616 | 163.3632
54 | 22 | 40.8376 | 41.2528 | 72.2656 | 1485.9768 | 169.6464
56 | 22 | 41.6552 | 42.0576 | 75.4072 | 1555.092 | 175.9296
58 | 22 | 42.4482 | 42.8389 | 78.5488 | 1624.2072 | 182.2128
60 | 22 | 43.2185 | 43.5982 | 81.6904 | 1693.3224 | 188.496
62 | 22 | 43.9676 | 44.3371 | 84.832 | 1762.4376 | 194.7792
0 | 22 | 44.7685 | 45.2 | 0 | 0 | 0
0 | 24 | 0 | 0 | 0 | 0 | 0
28 | 24 | 27 | 27.6718 | 30.2832 | 603.1872 | 87.9648
30 | 24 | 28.4741 | 29.2763 | 33.4248 | 678.5856 | 94.248
32 | 24 | 30.0225 | 30.7686 | 36.5664 | 753.984 | 100.5312
34 | 24 | 31.4673 | 32.1659 | 39.708 | 829.3824 | 106.8144
36 | 24 | 32.8238 | 33.4817 | 42.8496 | 904.7808 | 113.0976
38 | 24 | 34.1042 | 34.7267 | 45.9912 | 980.1792 | 119.3808
40 | 24 | 35.3182 | 35.9096 | 49.1328 | 1055.5776 | 125.664
42 | 24 | 36.4735 | 37.0374 | 52.2744 | 1130.976 | 131.9472
44 | 24 | 37.5767 | 38.116 | 55.416 | 1206.3744 | 138.2304
46 | 24 | 38.6332 | 39.1504 | 58.5576 | 1281.7728 | 144.5136
48 | 24 | 39.6477 | 40.1449 | 61.6992 | 1357.1712 | 150.7968
50 | 24 | 40.624 | 41.103 | 64.8408 | 1432.5696 | 157.08
52 | 24 | 41.5655 | 42.028 | 67.9824 | 1507.968 | 163.3632
54 | 24 | 42.4752 | 42.9224 | 71.124 | 1583.3664 | 169.6464
56 | 24 | 43.3556 | 43.7887 | 74.2656 | 1658.7648 | 175.9296
58 | 24 | 44.2089 | 44.6291 | 77.4072 | 1734.1632 | 182.2128
60 | 24 | 45.0372 | 45.4454 | 80.5488 | 1809.5616 | 188.496
62 | 24 | 45.8423 | 46.2392 | 83.6904 | 1884.96 | 194.7792
0 | 24 | 46.6696 | 47.1 | 0 | 0 | 0
0 | 26 | 0 | 0 | 0 | 0 | 0
30 | 26 | 29 | 29.6981 | 32.2832 | 694.2936 | 94.248
32 | 26 | 30.5123 | 31.3265 | 35.4248 | 775.9752 | 100.5312
34 | 26 | 32.0867 | 32.847 | 38.5664 | 857.6568 | 106.8144
36 | 26 | 33.5612 | 34.2754 | 41.708 | 939.3384 | 113.0976
38 | 26 | 34.9498 | 35.6241 | 44.8496 | 1021.02 | 119.3808
40 | 26 | 36.2637 | 36.9033 | 47.9912 | 1102.7016 | 125.664
42 | 26 | 37.5122 | 38.121 | 51.1328 | 1184.3832 | 131.9472
44 | 26 | 38.7025 | 39.284 | 54.2744 | 1266.0648 | 138.2304
46 | 26 | 39.841 | 40.398 | 57.416 | 1347.7464 | 144.5136
48 | 26 | 40.9328 | 41.4677 | 60.5576 | 1429.428 | 150.7968
50 | 26 | 41.9825 | 42.4973 | 63.6992 | 1511.1096 | 157.08
52 | 26 | 42.9938 | 43.4903 | 66.8408 | 1592.7912 | 163.3632
54 | 26 | 43.97 | 44.4498 | 69.9824 | 1674.4728 | 169.6464
56 | 26 | 44.914 | 45.3783 | 73.124 | 1756.1544 | 175.9296
58 | 26 | 45.8284 | 46.2784 | 76.2656 | 1837.836 | 182.2128
60 | 26 | 46.7153 | 47.1521 | 79.4072 | 1919.5176 | 188.496
62 | 26 | 47.5767 | 48.0012 | 82.5488 | 2001.1992 | 194.7792
64 | 26 | 48.4144 | 48.8275 | 85.6904 | 2082.8808 | 201.0624
0 | 26 | 49.2137 | 49.6 | 0 | 0 | 0
0 | 28 | 0 | 0 | 0 | 0 | 0
32 | 28 | 31 | 31.7213 | 34.2832 | 791.6832 | 100.5312
34 | 28 | 32.5461 | 33.3709 | 37.4248 | 879.648 | 106.8144
36 | 28 | 34.1437 | 34.9166 | 40.5664 | 967.6128 | 113.0976
38 | 28 | 35.6448 | 36.373 | 43.708 | 1055.5776 | 119.3808
40 | 28 | 37.0624 | 37.7517 | 46.8496 | 1143.5424 | 125.664
42 | 28 | 38.4069 | 39.062 | 49.9912 | 1231.5072 | 131.9472
44 | 28 | 39.6869 | 40.3117 | 53.1328 | 1319.472 | 138.2304
46 | 28 | 40.9094 | 41.5071 | 56.2744 | 1407.4368 | 144.5136
48 | 28 | 42.0804 | 42.6538 | 59.416 | 1495.4016 | 150.7968
50 | 28 | 43.205 | 43.7562 | 62.5576 | 1583.3664 | 157.08
52 | 28 | 44.2874 | 44.8185 | 65.6992 | 1671.3312 | 163.3632
54 | 28 | 45.3312 | 45.844 | 68.8408 | 1759.296 | 169.6464
56 | 28 | 46.3398 | 46.8357 | 71.9824 | 1847.2608 | 175.9296
58 | 28 | 47.316 | 47.7963 | 75.124 | 1935.2256 | 182.2128
60 | 28 | 48.2622 | 48.7281 | 78.2656 | 2023.1904 | 188.496
62 | 28 | 49.1806 | 49.6331 | 81.4072 | 2111.1552 | 194.7792
64 | 28 | 50.0731 | 50.5132 | 84.5488 | 2199.12 | 201.0624
0 | 28 | 50.9566 | 51.4 | 0 | 0 | 0
0 | 30 | 0 | 0 | 0 | 0 | 0
34 | 30 | 33.1 | 33.7421 | 36.2832 | 895.356 | 106.8144
36 | 30 | 34.5763 | 35.4105 | 39.4248 | 989.604 | 113.0976
38 | 30 | 36.1947 | 36.9789 | 42.5664 | 1083.852 | 119.3808
40 | 30 | 37.7198 | 38.4608 | 45.708 | 1178.1 | 125.664
42 | 30 | 39.1637 | 39.8667 | 48.8496 | 1272.348 | 131.9472
44 | 30 | 40.5361 | 41.2056 | 51.9912 | 1366.596 | 138.2304
46 | 30 | 41.8451 | 42.4846 | 55.1328 | 1460.844 | 144.5136
48 | 30 | 43.0973 | 43.71 | 58.2744 | 1555.092 | 150.7968
50 | 30 | 44.2985 | 44.887 | 61.416 | 1649.34 | 157.08
52 | 30 | 45.4534 | 46.0199 | 64.5576 | 1743.588 | 163.3632
54 | 30 | 46.5663 | 47.1126 | 67.6992 | 1837.836 | 169.6464
56 | 30 | 47.6406 | 48.1685 | 70.8408 | 1932.084 | 175.9296
58 | 30 | 48.6795 | 49.1905 | 73.9824 | 2026.332 | 182.2128
60 | 30 | 49.6858 | 50.1811 | 77.124 | 2120.58 | 188.496
62 | 30 | 50.6619 | 51.1427 | 80.2656 | 2214.828 | 194.7792
64 | 30 | 51.61 | 52.0772 | 83.4072 | 2309.076 | 201.0624
66 | 30 | 52.5319 | 52.9866 | 86.5488 | 2403.324 | 207.3456
0 | 30 | 53.4433 | 53.9 | 0 | 0 | 0
0 | 32 | 0 | 0 | 0 | 0 | 0
36 | 32 | 35.1 | 35.7607 | 38.2832 | 1005.312 | 113.0976
38 | 32 | 36.6034 | 37.4461 | 41.4248 | 1105.8432 | 119.3808
40 | 32 | 38.2406 | 39.0351 | 44.5664 | 1206.3744 | 125.664
42 | 32 | 39.7876 | 40.5401 | 47.708 | 1306.9056 | 131.9472
44 | 32 | 41.2555 | 41.971 | 50.8496 | 1407.4368 | 138.2304
46 | 32 | 42.6535 | 43.3361 | 53.9912 | 1507.968 | 144.5136
48 | 32 | 43.9892 | 44.6423 | 57.1328 | 1608.4992 | 150.7968
50 | 32 | 45.2689 | 45.8955 | 60.2744 | 1709.0304 | 157.08
52 | 32 | 46.4981 | 47.1006 | 63.416 | 1809.5616 | 163.3632
54 | 32 | 47.6813 | 48.2619 | 66.5576 | 1910.0928 | 169.6464
56 | 32 | 48.8225 | 49.3831 | 69.6992 | 2010.624 | 175.9296
58 | 32 | 49.9253 | 50.4675 | 72.8408 | 2111.1552 | 182.2128
60 | 32 | 50.9927 | 51.5179 | 75.9824 | 2211.6864 | 188.496
62 | 32 | 52.0274 | 52.5368 | 79.124 | 2312.2176 | 194.7792
64 | 32 | 53.0317 | 53.5265 | 82.2656 | 2412.7488 | 201.0624
66 | 32 | 54.0077 | 54.489 | 85.4072 | 2513.28 | 207.3456
68 | 32 | 54.9575 | 55.4259 | 88.5488 | 2613.8112 | 213.6288
0 | 32 | 55.963 | 56.5 | 0 | 0 | 0
0 | 34 | 0 | 0 | 0 | 0 | 0
38 | 34 | 37.1 | 37.7777 | 40.2832 | 1121.5512 | 119.3808
40 | 34 | 38.628 | 39.4783 | 43.4248 | 1228.3656 | 125.664
42 | 34 | 40.2822 | 41.086 | 46.5664 | 1335.18 | 131.9472
44 | 34 | 41.8491 | 42.6121 | 49.708 | 1441.9944 | 138.2304
46 | 34 | 43.339 | 44.066 | 52.8496 | 1548.8088 | 144.5136
48 | 34 | 44.7606 | 45.4553 | 55.9912 | 1655.6232 | 150.7968
50 | 34 | 46.121 | 46.7867 | 59.1328 | 1762.4376 | 157.08
52 | 34 | 47.4262 | 48.0657 | 62.2744 | 1869.252 | 163.3632
54 | 34 | 48.6814 | 49.2971 | 65.416 | 1976.0664 | 169.6464
56 | 34 | 49.891 | 50.485 | 68.5576 | 2082.8808 | 175.9296
58 | 34 | 51.059 | 51.6329 | 71.6992 | 2189.6952 | 182.2128
60 | 34 | 52.1885 | 52.7441 | 74.8408 | 2296.5096 | 188.496
62 | 34 | 53.2827 | 53.8212 | 77.9824 | 2403.324 | 194.7792
64 | 34 | 54.344 | 54.8668 | 81.124 | 2510.1384 | 201.0624
66 | 34 | 55.375 | 55.8831 | 84.2656 | 2616.9528 | 207.3456
68 | 34 | 56.3775 | 56.8719 | 87.4072 | 2723.7672 | 213.6288
70 | 34 | 57.3535 | 57.8351 | 90.5488 | 2830.5816 | 219.912
0 | 34 | 58.4176 | 59 | 0 | 0 | 0
0 | 36 | 0 | 0 | 0 | 0 | 0
40 | 36 | 39.2 | 39.7931 | 42.2832 | 1244.0736 | 125.664
42 | 36 | 40.6504 | 41.5077 | 45.4248 | 1357.1712 | 131.9472
44 | 36 | 42.32 | 43.1324 | 48.5664 | 1470.2688 | 138.2304
46 | 36 | 43.9052 | 44.6779 | 51.708 | 1583.3664 | 144.5136
48 | 36 | 45.4154 | 46.1529 | 54.8496 | 1696.464 | 150.7968
50 | 36 | 46.8588 | 47.5647 | 57.9912 | 1809.5616 | 157.08
52 | 36 | 48.2421 | 48.9195 | 61.1328 | 1922.6592 | 163.3632
54 | 36 | 49.5711 | 50.2226 | 64.2744 | 2035.7568 | 169.6464
56 | 36 | 50.8506 | 51.4786 | 67.416 | 2148.8544 | 175.9296
58 | 36 | 52.0849 | 52.6913 | 70.5576 | 2261.952 | 182.2128
60 | 36 | 53.2778 | 53.8644 | 73.6992 | 2375.0496 | 188.496
62 | 36 | 54.4326 | 55.0007 | 76.8408 | 2488.1472 | 194.7792
64 | 36 | 55.5519 | 56.1032 | 79.9824 | 2601.2448 | 201.0624
66 | 36 | 56.6386 | 57.174 | 83.124 | 2714.3424 | 207.3456
68 | 36 | 57.6947 | 58.2154 | 86.2656 | 2827.44 | 213.6288
70 | 36 | 58.7223 | 59.2292 | 89.4072 | 2940.5376 | 219.912
72 | 36 | 59.7233 | 60.2173 | 92.5488 | 3053.6352 | 226.1952
0 | 36 | 60.6587 | 61.1 | 0 | 0 | 0
0 | 38 | 0 | 0 | 0 | 0 | 0
de = 1.55 (π b2 / 4 + a b - b2)0.625/(π b + 2 a - 2 b)0.25
Note on T1: Ruskin: